## About
European standard EN 13363-1:2007
Solar protection devices combined with glazing -
Calculation of solar and light transmittance -
Part 1: Simplified method
Ontwikkeld door / Développé par
Wetenschappelijk en Technisch Centrum voor het Bouwbedrijf
Centre Scientifique et Technique de la Construction
Belgian Building Research Institute
in het kader van het Belgische project "KMO - normenantenne"
dans le cadre du projet belge "PME - antenne normes"
Read our discaimer on www.wtcb.be or www.cstc.be
Version 7.1

## Intro
EUROPEAN STANDARD EN 13363-1 : 2007
Solar protection devices combined with glazing - Calculation of solar and light transmittance - Part 1 : Simplified method
Dispositifs de protection solaire combinés à des vitrages - Calcul du facteur de transmission solaire et lumineuse - Partie 1 : Méthode simplifiée
The European standard EN 13363-1:2003+A1:2007 has been drawn up by the Technical Committee CEN/TC 89 "Thermal performance of buildings and building components".
This standard consists of two parts :
Part 1 : Simplified method (EN 13363-1)
Part 2 : Detailed calculation method (EN 13363-2)
The standard EN 13363-1 gives a simplified method based on the usually known data of the glazing, the U- and g-value, and the solar transmittance and reflectance of the solar protection device to estimate the total solar energy transmittance of a solar protection device combined with a glazing.
The results of this simplified method are approximate and generally tend to lie on the safe side for cooling load estimations.
The text of the standard EN 13363-1 must be consulted to know the exact application of this method.
This Excel sheet allows to carry out the calculations given in this standard in order to be able to estimate the total solar energy transmittance (g-value), the direct solar transmittance, the secondary internal heat transfer factor and the light transmittance of a solar protection device combined with glazing.
It contains the following sheets:
| · Some definitions are given in the sheet "Definitions". | Definitions
| · Typical data for glazings are indicated in the sheet "Glazing". | Glazing
| · Typical data for solar protection devices are indicated in the sheet "Solar prot. device". | Solar prot device
| · Data for solar protection devices have to be entered in the sheet "Solar prot device - Data". | Solar prot device - data
| · The worksheet "Results-1" gives the calculation of the total solar energy transmittance, the direct solar transmittance, the secondary internal heat transfer factor and the light transmittance of the specified solar protection devices combined with one specified glazing. | Results-1
| · The worksheet "Results-2" allows to see the effect of the g- and U-values of the glazing on the total solar energy transmittance of the combination solar protection device - glazing. | Results-2
| · The worksheet "Results-3" gives the calculation of the total solar energy transmittance (g-value), the direct solar transmittance and the secondary internal heat transfer factor of the combination of the specified solar protection devices with the 4 reference glazings defined in the standard EN 14501. | Results-3
| · The worksheet "Update" gives an explanation of the update of this version of the Excel tool compared to the previous one. | Update

## Definitions
Definitions
| te | The direct solar transmittance is the fraction of the incident solar radiation that is directly transmitted by the component (component can be : glazing, solar protection device, combination solar protection device-glazing, …)
| re | The direct solar reflectance is the fraction of the incident solar radiation that is directly reflected by the component.
| g | The total solar energy transmittance (solar factor) is the sum of the direct solar transmittance te and the indirect solar transmittance (fraction of the absorbed radiation that is reemitted to inside).This is the fraction of the total transmitted energy to the total incident solar radiation.
| U | The thermal transmittance is the density of heat flow rate through a component in the steady state divided by the temperature difference between the surroundings on each side of the component (in W/m² K)
| Fc | The Shading factor is the ratio of the solar factor of the combined glazing and solar protection device gtot to that of the glazing alone g
Characteristic data
Glazing
The glazing is characterised by its thermal transmittance Ug, its total solar energy transmittance g and its transmittance and reflectance values.
| Ug | Thermal transmittance of the glazing [W/m²K]
| g | Total solar energy transmittance [-]
| te | Direct solar transmittance of the glazing [-]
| re | Solar reflectance of the glazing (side facing the incident radiation) [-]
| r'e | Solar reflectance of the glazing (opposite side from incident radiation) [-]
| tv | Light transmittance of the glazing [-]
| rv | Light reflectance of the glazing (side facing the incident radiation) [-]
| r'v | Light reflectance of the glazing (opposite side from incident radiation) [-]
| qi | Secondary internal heat transfer factor [-] (qi = g - te)
Solar protection device
Solar protection devices are characterised by the following factors :
| te,B | (Direct) Solar transmittance of the solar protection device [-]
| re,B | Solar reflectance of the side of the solar protection device facing the incident radiation [-]
| r'e,B | Solar reflectance of the side of the solar protection device opposite from the incident radiation [-]
| ae,B | Solar absorptance of the side of the solar protection device facing the incident radiation [-]
| tv,B | Light transmittance of the solar protection device [-]
| rv,B | Light reflectance of the side of the solar protection device facing the incident radiation [-]
| r'v,B | Light reflectance of the side of the solar protection device opposite from the incident radiation [-]
Combination 'Glazing & Solar protection device'
The combination of the glazing and solar protection device is characterised by the following factors :
| g tot | Total solar energy transmittance [-]
| te,tot | Direct solar transmittance [-]
| qi,tot | Secondary internal heat transfer factor [-] (qi,tot = g,tot - te,tot)
| tv,tot | Light transmittance [-]
| Fc | Shading factor [-]

## Glazing
Data for typical glazing
(see Annex A in the standard EN 13363-1)
Product | Thermal | Total solar | Light | Light
| transmittance | energy | transmittance | reflectance
| W/(m²K) | transmittance
| Ug | g | tv | rv = r'v
Single clear glass | 5.7 | 0.85 | 0.9 | 0.08
Double clear glass | 3 | 0.75 | 0.82 | 0.15
Triple clear glass | 2 | 0.65 | 0.75 | 0.2
Double clear glass with low emissivity coating | 1.6 | 0.7 | 0.75 | 0.17
These data are on the safe side for cooling load estimations.
These data are given for information.
The real data (U-value, g-value, light and solar transmittance and reflectance) for the glazing with which you want to combine the solar protection devices have to be introduced in the worsheet "Results-1".

## Solar prot device
Typical data for solar protection devices
(see Annex A of the standard EN 13363-1)
The next table gives typical values of transmittance and reflectance of solar protection device materials. These are indicative values given for information.
|  | White | Pastel | Dark | Black
Transmittance te,B |  | Reflectance re,B
Opaque | 0 | 0.7 | 0.5 | 0.3 | 0.1
Medium translucent | 0.2 | 0.6 | 0.4 | 0.2 | 0.1
High translucent | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
The absorptance, ae,B, is equal to 1 - te,B - re,B

## Solar prot device - data
Data for solar protection device
Please enter the characteristic data of your solar protection devices in the following table :
Where:
te,B * | (Direct) Solar transmittance of the solar protection device [-] | [6 empty] | * Required for the calculation of the g-value
re,B * | Solar reflectance of the side of the solar protection device facing the incident radiation [-] | [6 empty] | * Required for the calculation of the g-value
r'e,B | Solar reflectance of the side of the solar protection device opposite from the incident radiation [-]
ae,B | Solar absorptance of the side of the solar protection device facing the incident radiation [-]
tv,B | Light transmittance of the solar protection device [-]
rv,B | Light reflectance of the side of the solar protection device facing the incident radiation [-]
r'v,B | Light reflectance of the side of the solar protection device opposite from the incident radiation [-]
Prot. | Name of the solar protection device | te,B | re,B | r'e,B | ae,B | tv,B | rv,B | r'v,B
nr
1 | Opaque - White | 0 | 0.7 | 0.7 | 0.3 | 0 | 0.7 | 0.7
2 | Opaque - Pastel | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5
3 | Opaque - Dark | 0 | 0.3 | 0.3 | 0.7 | 0 | 0.3 | 0.3
4 | Opaque - Black | 0 | 0.1 | 0.1 | 0.9 | 0 | 0.1 | 0.1
5 | Medium translucent - White | 0.2 | 0.6 | 0.6 | 0.2 | 0.2 | 0.6 | 0.6
6 | Medium translucent - Pastel | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4
7 | Medium translucent - Dark | 0.2 | 0.2 | 0.2 | 0.6 | 0.2 | 0.2 | 0.2
8 | Medium translucent - Black | 0.2 | 0.1 | 0.1 | 0.7 | 0.2 | 0.1 | 0.1
9 | High translucent - White | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.4
10 | High translucent - Pastel | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3
11 | High translucent - Dark | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2
12 | High translucent - Black | 0.4 | 0.1 | 0.1 | 0.5 | 0.4 | 0.1 | 0.1
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100

## Results-1
Please enter the characteristic data of the glazing with which you want to combine the solar protection device :
Glazing |  | Name | Glazing Z
|  | U-value * | 1.1 | (thermal transmittance in [W/(m²K)]) | [5 empty] | * Required for the calculation of the g-value
|  | g-value * | 0.85 | (total solar energy transmittance) | [5 empty] | * Required for the calculation of the g-value
|  | t e | 0.27 | (solar transmittance)
|  | r e | 0.29 | (solar reflectance)
|  | r' e | 0.38 | (solar reflectance)
|  | t v | 0.27 | (light transmittance)
|  | r v | 0.29 | (light reflectance)
|  | r' v | 0.38 | (light reflectance)
The following table gives the total solar energy transmittance gtot, the direct solar transmittance te,tot, the secondary internal heat transfer factor qi,tot and the light transmittance tv,tot for the combination of the specified glazing (see characteristics above) and solar protection devices (see characteristics in sheet "Solar prot. device-data") according to the standard EN 13363-1. Three cases are distinguished : external solar prot. device, internal solar prot. device and integrated solar prot. device (between glass panes) :
[11 empty] | gtot |  |  | te, tot |  | qi,tot |  | tv, tot |  | Fc
Comb. | Name of the combination glazing + blind |  |  | te,B | re,B | r'e,B | ae,B | tv,B | rv,B | r'v,B | External | Internal | Integrated | External | Internal | External | Internal | External | Internal | External | Internal | Integrated | G1 | 5
nr | [10 empty] | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | prot.dev. | G2 ext | 10
1 | Glazing Z + Opaque - White |  |  | 0 | 0.7 | 0.7 | 0.3 | 0 | 0.7 | 0.7 | 0.024812 | 0.33523 | 0.09236 | 0 | 0 | 0.024812 | 0.33523 | 0 | 0 | 0.029191 | 0.39439 | 0.10866 | G2 int | 30
2 | Glazing Z + Opaque - Pastel |  |  | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.041353 | 0.47372 | 0.13113 | 0 | 0 | 0.041353 | 0.47372 | 0 | 0 | 0.048651 | 0.55732 | 0.15427 | G3 | 3
3 | Glazing Z + Opaque - Dark |  |  | 0 | 0.3 | 0.3 | 0.7 | 0 | 0.3 | 0.3 | 0.057895 | 0.6122 | 0.1699 | 0 | 0 | 0.057895 | 0.6122 | 0 | 0 | 0.068111 | 0.72024 | 0.19988 | G ext | 0.82707
4 | Glazing Z + Opaque - Black |  |  | 0 | 0.1 | 0.1 | 0.9 | 0 | 0.1 | 0.1 | 0.074436 | 0.75069 | 0.20866 | 0 | 0 | 0.074436 | 0.75069 | 0 | 0 | 0.087572 | 0.88317 | 0.24549 | G int | 1.0611
5 | Glazing Z + Medium translucent - White |  |  | 0.2 | 0.6 | 0.6 | 0.2 | 0.2 | 0.6 | 0.6 | 0.1915 | 0.41049 | 0.23613 | 0.065375 | 0.069948 | 0.12613 | 0.34054 | 0.065375 | 0.069948 | 0.2253 | 0.48293 | 0.2778 | G between | 0.80488
6 | Glazing Z + Medium translucent - Pastel |  |  | 0.2 | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.20805 | 0.54897 | 0.2749 | 0.061086 | 0.063679 | 0.14696 | 0.4853 | 0.061086 | 0.063679 | 0.24476 | 0.64585 | 0.32341
7 | Glazing Z + Medium translucent - Dark |  |  | 0.2 | 0.2 | 0.2 | 0.6 | 0.2 | 0.2 | 0.2 | 0.22459 | 0.68746 | 0.31367 | 0.057325 | 0.058442 | 0.16726 | 0.62902 | 0.057325 | 0.058442 | 0.26422 | 0.80878 | 0.36902
8 | Glazing Z + Medium translucent - Black |  |  | 0.2 | 0.1 | 0.1 | 0.7 | 0.2 | 0.1 | 0.1 | 0.23286 | 0.7567 | 0.33305 | 0.055613 | 0.056133 | 0.17724 | 0.70057 | 0.055613 | 0.056133 | 0.27395 | 0.89024 | 0.39183
9 | Glazing Z + High translucent - White |  |  | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.4 | 0.36647 | 0.55499 | 0.39929 | 0.12217 | 0.12736 | 0.24429 | 0.42763 | 0.12217 | 0.12736 | 0.43114 | 0.65293 | 0.46976
10 | Glazing Z + High translucent - Pastel |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.37474 | 0.62423 | 0.41868 | 0.11829 | 0.1219 | 0.25645 | 0.50233 | 0.11829 | 0.1219 | 0.44087 | 0.73439 | 0.49256
11 | Glazing Z + High translucent - Dark |  |  | 0.4 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.38301 | 0.69347 | 0.43806 | 0.11465 | 0.11688 | 0.26836 | 0.57659 | 0.11465 | 0.11688 | 0.4506 | 0.81585 | 0.51537
12 | Glazing Z + High translucent - Black |  |  | 0.4 | 0.1 | 0.1 | 0.5 | 0.4 | 0.1 | 0.1 | 0.39128 | 0.76272 | 0.45745 | 0.11123 | 0.11227 | 0.28005 | 0.65045 | 0.11123 | 0.11227 | 0.46033 | 0.89732 | 0.53817
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
Note on O31: Solar factor (g-value) of the combination "glazing + solar protection device"
Note on R31: Direct solar transmittance of the combination "glazing + solar protection device"
Note on T31: Secondary internal heat transfer factor of the combination "glazing + solar protection device"
Note on V31: Light transmittance of the combination "glazing + solar protection device"
Note on Y31: Shading factor

## Results-2
The following chart gives the total solar energy transmittance gtotal for the combination glazing - solar protection device. The solar protection device can be external, internal or integrated between the panes. The effect of different U-values and g-values of the glazing on the total solar energy transmittance of the combination is shown.
Choose the solar protection device that you want to analyse :
[5 empty] | (See sheet "Solar prot device - data") | Glazing | U1 | 1.1 | (U = thermal transmittance in [W/(m²K)])
9 | [6 empty] | U2 | 3
[7 empty] | U3 | 5.8
Blind | Name: | High translucent - White |  |  |  | Blind | n° | 9 |  |  | G1 | 5 | W/m²K
| te,B : | 0.4 |  |  |  |  | Name | High translucent - White |  |  | G2 ext | 10 | W/m²K
| re,B : | 0.4 |  |  |  |  | te,B | 0.4 |  |  | G2 int | 30 | W/m²K
| ae,B : | 0.2 |  |  |  |  | re,B | 0.4 |  |  | G3 | 3 | W/m²K
[7 empty] | a e,B | 0.2
Choose 3 U-values for the glazing :
Glazing | Ug 1 = | 1.1 | W/m²K | Show | Internal
| Ug 2 = | 3 | W/m²K |  | External |  |  |  | External, | External, | External, |  | Internal, | Internal, | Internal, |  | Between, | Between, | Between,
| Ug 3 = | 5.8 | W/m²K |  | Between |  |  |  | U = 1,1 | U = 3 | U = 5,8 |  | U = 1,1 | U = 3 | U = 5,8 |  | U = 1,1 | U = 3 | U = 5,8
[7 empty] | U glazing |  | 1.1 | 3 | 5.8 |  | 1.1 | 3 | 5.8 |  | 1.1 | 3 | 5.8
[7 empty] | G |  | 0.82707 | 1.5789 | 2.1168 |  | 1.0611 | 2.7273 | 4.8603 |  | 0.80488 | 1.5 | 1.9773
g glazing
[7 empty] | 0.15 |  | 0.13278 | 0.19895 | 0.24628 |  | 0.13994 | 0.13827 | 0.13614 |  | 0.081732 | 0.1005 | 0.11339
[7 empty] | 0.2 |  | 0.14947 | 0.21263 | 0.25781 |  | 0.18259 | 0.18036 | 0.17752 |  | 0.1079 | 0.132 | 0.14855
[7 empty] | 0.25 |  | 0.16617 | 0.22632 | 0.26934 |  | 0.22323 | 0.22045 | 0.2169 |  | 0.13354 | 0.1625 | 0.18239
[7 empty] | 0.3 |  | 0.18286 | 0.24 | 0.28088 |  | 0.26188 | 0.25855 | 0.25428 |  | 0.15863 | 0.192 | 0.21491
[7 empty] | 0.35 |  | 0.19955 | 0.25368 | 0.29241 |  | 0.29852 | 0.29464 | 0.28966 |  | 0.1832 | 0.2205 | 0.24611
[7 empty] | 0.4 |  | 0.21624 | 0.26737 | 0.30394 |  | 0.33317 | 0.32873 | 0.32304 |  | 0.20722 | 0.248 | 0.276
[7 empty] | 0.45 |  | 0.23293 | 0.28105 | 0.31547 |  | 0.36582 | 0.36082 | 0.35442 |  | 0.23071 | 0.2745 | 0.30457
[7 empty] | 0.5 |  | 0.24962 | 0.29474 | 0.32701 |  | 0.39646 | 0.39091 | 0.3838 |  | 0.25366 | 0.3 | 0.33182
[7 empty] | 0.55 |  | 0.26632 | 0.30842 | 0.33854 |  | 0.42511 | 0.419 | 0.41118 |  | 0.27607 | 0.3245 | 0.35775
[7 empty] | 0.6 |  | 0.28301 | 0.32211 | 0.35007 |  | 0.45176 | 0.44509 | 0.43656 |  | 0.29795 | 0.348 | 0.38236
[7 empty] | 0.65 |  | 0.2997 | 0.33579 | 0.36161 |  | 0.4764 | 0.46918 | 0.45994 |  | 0.31929 | 0.3705 | 0.40566
[7 empty] | 0.7 |  | 0.31639 | 0.34947 | 0.37314 |  | 0.49905 | 0.49127 | 0.48132 |  | 0.3401 | 0.392 | 0.42764
[7 empty] | 0.75 |  | 0.33308 | 0.36316 | 0.38467 |  | 0.51969 | 0.51136 | 0.5007 |  | 0.36037 | 0.4125 | 0.4483
[7 empty] | 0.8 |  | 0.34977 | 0.37684 | 0.3962 |  | 0.53834 | 0.52945 | 0.51808 |  | 0.3801 | 0.432 | 0.46764
[7 empty] | 0.85 |  | 0.36647 | 0.39053 | 0.40774 |  | 0.55499 | 0.54555 | 0.53346 |  | 0.39929 | 0.4505 | 0.48566
[9 empty] | External,U = 1,1 | External,U = 3 | External,U = 5,8 |  | Internal,U = 1,1 | Internal,U = 3 | Internal,U = 5,8
[7 empty] | Toont |  | TRUE |  |  | g | TRUE |  |  | g | FALSE
[7 empty] | 0.15 |  | 0.13278 | 0.19895 | 0.24628 | 0.15 | 0.13994 | 0.13827 | 0.13614
[7 empty] | 0.2 |  | 0.14947 | 0.21263 | 0.25781 | 0.2 | 0.18259 | 0.18036 | 0.17752
[7 empty] | 0.25 |  | 0.16617 | 0.22632 | 0.26934 | 0.25 | 0.22323 | 0.22045 | 0.2169
[7 empty] | 0.3 |  | 0.18286 | 0.24 | 0.28088 | 0.3 | 0.26188 | 0.25855 | 0.25428
[7 empty] | 0.35 |  | 0.19955 | 0.25368 | 0.29241 | 0.35 | 0.29852 | 0.29464 | 0.28966
[7 empty] | 0.4 |  | 0.21624 | 0.26737 | 0.30394 | 0.4 | 0.33317 | 0.32873 | 0.32304
[7 empty] | 0.45 |  | 0.23293 | 0.28105 | 0.31547 | 0.45 | 0.36582 | 0.36082 | 0.35442
[7 empty] | 0.5 |  | 0.24962 | 0.29474 | 0.32701 | 0.5 | 0.39646 | 0.39091 | 0.3838
[7 empty] | 0.55 |  | 0.26632 | 0.30842 | 0.33854 | 0.55 | 0.42511 | 0.419 | 0.41118
[7 empty] | 0.6 |  | 0.28301 | 0.32211 | 0.35007 | 0.6 | 0.45176 | 0.44509 | 0.43656
[7 empty] | 0.65 |  | 0.2997 | 0.33579 | 0.36161 | 0.65 | 0.4764 | 0.46918 | 0.45994
[7 empty] | 0.7 |  | 0.31639 | 0.34947 | 0.37314 | 0.7 | 0.49905 | 0.49127 | 0.48132
[7 empty] | 0.75 |  | 0.33308 | 0.36316 | 0.38467 | 0.75 | 0.51969 | 0.51136 | 0.5007
[7 empty] | 0.8 |  | 0.34977 | 0.37684 | 0.3962 | 0.8 | 0.53834 | 0.52945 | 0.51808
[7 empty] | 0.85 |  | 0.36647 | 0.39053 | 0.40774 | 0.85 | 0.55499 | 0.54555 | 0.53346

## Results-3
Calculation of the total solar energy transmittance (gtot), the direct solar transmittance te,tot and the secondary internal heat transfer factor qi,tot for the combination of the reference glazings indicated in the standard EN 14501:2005 and the specified solar protection devices (see characteristics in sheet "Solar prot. device-data")
EN 14501 : Blinds and shutters - Thermal and visual comfort - Performance characteristics and classification
Four reference glazings are specified in the annex A of EN 14501 :
1. Glazing A : clear single glazing (4 mm)
2. Glazing B : clear double glazing (4 / 12 / 4), space filled with air
3. Glazing C : double glazing (4 / 16 / 4), with low emissivity coating in position 3, space filled with argon
4. Glazing D : Reflective double glazing (4 / 16 / 4), with a low emissivity soft coating in position 2, space filled with Argon
|  | U (W/m²K) | g (-) | te | re | r'e
| Glazing A | 5.8 | 0.85 | 0.83 | 0.08 | 0.08
| Glazing B | 2.9 | 0.76 | 0.69 | 0.14 | 0.14
| Glazing C | 1.2 | 0.59 | 0.49 | 0.29 | 0.27
| Glazing D | 1.1 | 0.32 | 0.27 | 0.29 | 0.38
[49 empty] | Glazing A | Glazing B | Glazing C | Glazing D
[8 empty] | SOLAR FACTOR gtot | [11 empty] | DIRECT SOLAR TRANSMITTANCE te,tot | [7 empty] | SECONDARY INTERNAL HEAT TRANSFER FACTOR qi,tot | [7 empty] | SHADING FACTOR Fc | [11 empty] | U | 5.8 | 2.9 | 1.2 | 1.1
[8 empty] | External prot. device |  |  |  | Internal prot. device |  |  |  | Integrated prot. device |  |  |  | External prot. device |  |  |  | Internal prot. device |  |  |  | External prot. device |  |  |  | Internal prot. device |  |  |  | External prot. device |  |  |  | Internal prot. device |  |  |  | Integrated prot. device |  |  |  | g | 0.85 | 0.76 | 0.59 | 0.32
Comb. | Name of the combination glazing + blind |  |  | te,B | re,B | r'e,B | ae,B | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | prot. dev. + | G1 | 5 | 5 | 5 | 5
nr | [7 empty] | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | Glazing A | Glazing B | Glazing C | Glazing D | G2 ext | 10 | 10 | 10 | 10
1 | Glazing + Opaque - White |  |  | 0 | 0.7 | 0.7 | 0.3 | 0.063504 | 0.046524 | 0.026471 | 0.024812 | 0.30294 | 0.33558 | 0.33952 | 0.24492 | 0.22689 | 0.17483 | 0.098951 | 0.066622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063504 | 0.046524 | 0.026471 | 0.024812 | 0.30294 | 0.33558 | 0.33952 | 0.24492 | 0.07471 | 0.061216 | 0.044865 | 0.077538 | 0.3564 | 0.44156 | 0.57546 | 0.76539 | 0.26693 | 0.23003 | 0.16771 | 0.2082 | G2 int | 30 | 30 | 30 | 30
2 | Glazing + Opaque - Pastel |  |  | 0 | 0.5 | 0.5 | 0.5 | 0.10584 | 0.07754 | 0.044118 | 0.041353 | 0.4199 | 0.4377 | 0.4046 | 0.26314 | 0.32213 | 0.23161 | 0.11884 | 0.072117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10584 | 0.07754 | 0.044118 | 0.041353 | 0.4199 | 0.4377 | 0.4046 | 0.26314 | 0.12452 | 0.10203 | 0.074776 | 0.12923 | 0.49399 | 0.57593 | 0.68577 | 0.82232 | 0.37898 | 0.30475 | 0.20143 | 0.22537 | G3 | 3 | 3 | 3 | 3
3 | Glazing + Opaque - Dark |  |  | 0 | 0.3 | 0.3 | 0.7 | 0.14818 | 0.10856 | 0.061765 | 0.057895 | 0.53685 | 0.53983 | 0.46969 | 0.28136 | 0.41737 | 0.28839 | 0.13873 | 0.077612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14818 | 0.10856 | 0.061765 | 0.057895 | 0.53685 | 0.53983 | 0.46969 | 0.28136 | 0.17432 | 0.14284 | 0.10469 | 0.18092 | 0.63159 | 0.7103 | 0.79608 | 0.87924 | 0.49102 | 0.37946 | 0.23514 | 0.24254 | G ext | 2.1168 | 1.5508 | 0.88235 | 0.82707
4 | Glazing + Opaque - Black |  |  | 0 | 0.1 | 0.1 | 0.9 | 0.19051 | 0.13957 | 0.079412 | 0.074436 | 0.65381 | 0.64195 | 0.53477 | 0.29957 | 0.51261 | 0.34517 | 0.15863 | 0.083106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19051 | 0.13957 | 0.079412 | 0.074436 | 0.65381 | 0.64195 | 0.53477 | 0.29957 | 0.22413 | 0.18365 | 0.1346 | 0.23261 | 0.76919 | 0.84467 | 0.90638 | 0.93617 | 0.60307 | 0.45417 | 0.26886 | 0.25971 | G int | 4.8603 | 2.6444 | 1.1538 | 1.0611
5 | Glazing + Medium translucent - White |  |  | 0.2 | 0.6 | 0.6 | 0.2 | 0.22504 | 0.1979 | 0.15012 | 0.10304 | 0.38896 | 0.40004 | 0.3766 | 0.2563 | 0.33247 | 0.2805 | 0.19318 | 0.1162 | 0.17437 | 0.15066 | 0.11864 | 0.065375 | 0.17437 | 0.15066 | 0.11695 | 0.069948 | 0.050667 | 0.047249 | 0.031474 | 0.037662 | 0.21459 | 0.24939 | 0.25966 | 0.18635 | 0.26475 | 0.2604 | 0.25444 | 0.32199 | 0.4576 | 0.52637 | 0.63831 | 0.80093 | 0.39114 | 0.36908 | 0.32743 | 0.36312 | G between | 1.9773 | 1.4746 | 0.85714 | 0.80488
6 | Glazing + Medium translucent - Pastel |  |  | 0.2 | 0.4 | 0.4 | 0.4 | 0.26737 | 0.22892 | 0.16776 | 0.11958 | 0.50592 | 0.50216 | 0.44168 | 0.27451 | 0.4277 | 0.33729 | 0.21307 | 0.12169 | 0.17149 | 0.14619 | 0.11086 | 0.061086 | 0.17149 | 0.14619 | 0.10987 | 0.063679 | 0.095885 | 0.082733 | 0.056905 | 0.058493 | 0.33443 | 0.35598 | 0.33182 | 0.21083 | 0.31456 | 0.30121 | 0.28435 | 0.37368 | 0.5952 | 0.66074 | 0.74862 | 0.85785 | 0.50318 | 0.4438 | 0.36114 | 0.38029
7 | Glazing + Medium translucent - Dark |  |  | 0.2 | 0.2 | 0.2 | 0.6 | 0.30971 | 0.25994 | 0.18541 | 0.13612 | 0.62287 | 0.60429 | 0.50676 | 0.29273 | 0.52294 | 0.39407 | 0.23297 | 0.12719 | 0.1687 | 0.14198 | 0.10403 | 0.057325 | 0.1687 | 0.14198 | 0.10359 | 0.058442 | 0.14101 | 0.11796 | 0.081378 | 0.078795 | 0.45418 | 0.46231 | 0.40317 | 0.23429 | 0.36436 | 0.34202 | 0.31426 | 0.42538 | 0.73279 | 0.79511 | 0.85892 | 0.91478 | 0.61523 | 0.51851 | 0.39486 | 0.39746
8 | Glazing + Medium translucent - Black |  |  | 0.2 | 0.1 | 0.1 | 0.7 | 0.33088 | 0.27544 | 0.19424 | 0.14439 | 0.68135 | 0.65535 | 0.53931 | 0.30184 | 0.57056 | 0.42246 | 0.24291 | 0.12994 | 0.16734 | 0.13996 | 0.10093 | 0.055613 | 0.16734 | 0.13996 | 0.10072 | 0.056133 | 0.16354 | 0.13548 | 0.093308 | 0.088778 | 0.51401 | 0.51539 | 0.43859 | 0.2457 | 0.38927 | 0.36243 | 0.32921 | 0.45122 | 0.80159 | 0.8623 | 0.91408 | 0.94324 | 0.67125 | 0.55586 | 0.41171 | 0.40605
9 | Glazing + High translucent - White |  |  | 0.4 | 0.4 | 0.4 | 0.2 | 0.40774 | 0.36479 | 0.28259 | 0.18953 | 0.53346 | 0.51556 | 0.44622 | 0.27678 | 0.48566 | 0.41457 | 0.29736 | 0.16852 | 0.34298 | 0.29237 | 0.22172 | 0.12217 | 0.34298 | 0.29237 | 0.21973 | 0.12736 | 0.064762 | 0.072419 | 0.060869 | 0.067362 | 0.19048 | 0.22319 | 0.22649 | 0.14942 | 0.47969 | 0.47999 | 0.47896 | 0.59229 | 0.6276 | 0.67837 | 0.75631 | 0.86493 | 0.57136 | 0.54549 | 0.504 | 0.52663
10 | Glazing + High translucent - Pastel |  |  | 0.4 | 0.3 | 0.3 | 0.3 | 0.42891 | 0.3803 | 0.29141 | 0.1978 | 0.59194 | 0.56662 | 0.47876 | 0.28588 | 0.53328 | 0.44296 | 0.30731 | 0.17127 | 0.34016 | 0.2881 | 0.21468 | 0.11829 | 0.34016 | 0.2881 | 0.21328 | 0.1219 | 0.088741 | 0.092199 | 0.076735 | 0.079513 | 0.25177 | 0.27852 | 0.26549 | 0.16399 | 0.50459 | 0.50039 | 0.49392 | 0.61814 | 0.6964 | 0.74556 | 0.81146 | 0.89339 | 0.62739 | 0.58285 | 0.52086 | 0.53522
11 | Glazing + High translucent - Dark |  |  | 0.4 | 0.2 | 0.2 | 0.4 | 0.45007 | 0.39581 | 0.30024 | 0.20608 | 0.65042 | 0.61768 | 0.5113 | 0.29499 | 0.5809 | 0.47135 | 0.31725 | 0.17402 | 0.3374 | 0.28395 | 0.20807 | 0.11465 | 0.3374 | 0.28395 | 0.20719 | 0.11688 | 0.11267 | 0.11186 | 0.092167 | 0.091426 | 0.31302 | 0.33373 | 0.30411 | 0.17811 | 0.5295 | 0.5208 | 0.50887 | 0.64398 | 0.7652 | 0.81274 | 0.86662 | 0.92185 | 0.68341 | 0.6202 | 0.53771 | 0.5438
12 | Glazing + High translucent - Black |  |  | 0.4 | 0.1 | 0.1 | 0.5 | 0.47124 | 0.41132 | 0.30906 | 0.21435 | 0.7089 | 0.66874 | 0.54384 | 0.3041 | 0.62852 | 0.49975 | 0.3272 | 0.17676 | 0.33468 | 0.27992 | 0.20185 | 0.11123 | 0.33468 | 0.27992 | 0.20144 | 0.11227 | 0.13656 | 0.1314 | 0.10721 | 0.10312 | 0.37422 | 0.38883 | 0.3424 | 0.19183 | 0.5544 | 0.5412 | 0.52383 | 0.66983 | 0.83399 | 0.87993 | 0.92177 | 0.95032 | 0.73943 | 0.65756 | 0.55457 | 0.55239
13 | Glazing +
14 | Glazing +
15 | Glazing +
16 | Glazing +
17 | Glazing +
18 | Glazing +
19 | Glazing +
20 | Glazing +
21 | Glazing +
22 | Glazing +
23 | Glazing +
24 | Glazing +
25 | Glazing +
26 | Glazing +
27 | Glazing +
28 | Glazing +
29 | Glazing +
30 | Glazing +
31 | Glazing +
32 | Glazing +
33 | Glazing +
34 | Glazing +
35 | Glazing +
36 | Glazing +
37 | Glazing +
38 | Glazing +
39 | Glazing +
40 | Glazing +
41 | Glazing +
42 | Glazing +
43 | Glazing +
44 | Glazing +
45 | Glazing +
46 | Glazing +
47 | Glazing +
48 | Glazing +
49 | Glazing +
50 | Glazing +
51 | Glazing +
52 | Glazing +
53 | Glazing +
54 | Glazing +
55 | Glazing +
56 | Glazing +
57 | Glazing +
58 | Glazing +
59 | Glazing +
60 | Glazing +
61 | Glazing +
62 | Glazing +
63 | Glazing +
64 | Glazing +
65 | Glazing +
66 | Glazing +
67 | Glazing +
68 | Glazing +
69 | Glazing +
70 | Glazing +
71 | Glazing +
72 | Glazing +
73 | Glazing +
74 | Glazing +
75 | Glazing +
76 | Glazing +
77 | Glazing +
78 | Glazing +
79 | Glazing +
80 | Glazing +
81 | Glazing +
82 | Glazing +
83 | Glazing +
84 | Glazing +
85 | Glazing +
86 | Glazing +
87 | Glazing +
88 | Glazing +
89 | Glazing +
90 | Glazing +
91 | Glazing +
92 | Glazing +
93 | Glazing +
94 | Glazing +
95 | Glazing +
96 | Glazing +
97 | Glazing +
98 | Glazing +
99 | Glazing +
100 | Glazing +
Note on L26: Solar factor (g-value) of the combination 'glazing + solar protection device'
Note on Y26: Direct solar transmittance of the combination 'glazing + solar protection device'
Note on AH26: Secondary internal heat transfer factor of the combination 'glazing + solar protection device'
Note on AQ26: Shading factor

## Update
Version # | Date | Main updates
Version 5 | 2007-12-12 | correction cel E18 of the sheet 'Results-2'
Version 6 | 2008-05-15 | Adaptations of the formulae in order to be conform with the new version of the standard EN13363-1 (2007)
Version 7 | 2008-07-24 | The calculation of the 'shading factor' Fc has been added
Version 7.1 | 2021-10-22 | Sends statistical data to BBRI